## Step Drawdown Test
STEP DRAWDOWN TEST | SDT |  |  |  |  | FIVE HOUR TEST
Type of pump | WA 110-2
H.P | 60 | HP
Capacity | 185 | lpm
Diameter of delivery pipe | 100 | mm
Date of test | 29/06/2025
Static Water Level | 6.82 | (m) b.m.p
M.P Top of well casing |  | (m) agl
Table 1: Step Drawdown Test on CDW 52
Based on SDT and APT | Steps | Time in Hours | Pumping Water Level in m [b.m.p] | Drawdown (S) in m | Discharge (Q) in l.p.m. | Remarks
|  | 14:00 | 6.82
| Step I | 14:01 | 9.68 | 2.86 | 157.8 | Pumping started at 14:00
|  | 14:02 | 10.02 | 3.2 | 157.8
|  | 14:03 | 10.71 | 3.89 | 157.8
|  | 14:04 | 10.92 | 4.1 | 157.8
|  | 14:05 | 11.12 | 4.3 | 157.8
|  | 14:06 | 12.02 | 5.2 | 157.8 | Atm temp
|  | 14:07 | 13.22 | 6.4 | 157.8 | Water temp
|  | 14:08 | 13.93 | 7.11 | 157.8
|  | 14:09 | 14.32 | 7.5 | 157.8
|  | 14:10 | 14.56 | 7.74 | 157.8
|  | 14:11 | 14.78 | 7.96 | 157.8
|  | 14:12 | 14.99 | 8.17 | 157.8
|  | 14:13 | 15.88 | 9.06 | 157.8
|  | 14:14 | 16.1 | 9.28 | 157.8 | Water crystal clear
|  | 14:15 | 16.54 | 9.72 | 157.8
|  | 14:16 | 16.96 | 10.14 | 157.8
|  | 14:17 | 17.29 | 10.47 | 157.8
|  | 14:18 | 17.58 | 10.76 | 157.8
|  | 14:19 | 17.84 | 11.02 | 157.8
|  | 14:20 | 18.05 | 11.23 | 157.8
|  | 14:25 | 18.66 | 11.84 | 157.8
|  | 14:30 | 18.91 | 12.09 | 157.8
|  | 14:40 | 19.33 | 12.51 | 157.8
|  | 14:50 | 19.24 | 12.42 | 157.8
|  | 15:00 | 19.03 | 12.21 | 157.8
| Step II | 15:01 | 19.18 | 12.36 | 207
|  | 15:02 | 19.76 | 12.94 | 207
|  | 15:03 | 19.81 | 12.99 | 207 | Water crystal clear
|  | 15:04 | 20.08 | 13.26 | 207
|  | 15:05 | 20.8 | 13.98 | 207
|  | 15:06 | 21.03 | 14.21 | 207
|  | 15:07 | 22.2 | 15.38 | 207
|  | 15:08 | 24.05 | 17.23 | 207
|  | 15:09 | 24.89 | 18.07 | 207
|  | 15:10 | 26.06 | 19.24 | 207
|  | 15:11 | 26.83 | 20.01 | 207
|  | 15:12 | 28.1 | 21.28 | 207
|  | 15:13 | 29.68 | 22.86 | 207
|  | 15:14 | 30.28 | 23.46 | 207
|  | 15:15 | 31.8 | 24.98 | 207
|  | 15:16 | 32.28 | 25.46 | 207
|  | 15:17 | 33.95 | 27.13 | 207
|  | 15:18 | 35.93 | 29.11 | 207
|  | 15:19 | 38.08 | 31.26 | 207
|  | 15:20 | 41.11 | 34.29 | 207
|  | 15:25 | 45.28 | 38.46 | 207
|  | 15:30 | 49.32 | 42.5 | 207
|  | 15:40 | 59.34 | 52.52 | 207
|  | 15:50 | 63.83 | 57.01 | 207
|  | 16:00 | 66.86 | 60.04 | 207
| Step III | 16:01 | 68.4 | 61.58 | 240
|  | 16:02 | 69.12 | 62.3 | 240
|  | 16:03 | 69.92 | 63.1 | 240
|  | 16:04 | 70.79 | 63.97 | 240
|  | 16:05 | 71.87 | 65.05 | 240
|  | 16:06 | 73.24 | 66.42 | 240 | Water crystal clear
|  | 16:07 | 73.98 | 67.16 | 240 | Atm temp
|  | 16:08 | 74.98 | 68.16 | 240 | Water temp
|  | 16:09 | 75.38 | 68.56 | 240 | Test concluded at 16:40hrs
|  | 16:10 | 75.74 | 68.92 | 240
|  | 16:11 | 76.46 | 69.64 | 240
|  | 16:12 | 77.67 | 70.85 | 240
|  | 16:13 | 78.67 | 71.85 | 240
|  | 16:14 | 79.92 | 73.1 | 240
|  | 16:15 | 80.86 | 74.04 | 240
|  | 16:16 | 81.76 | 74.94 | 240
|  | 16:17 | 83.15 | 76.33 | 240
|  | 16:18 | 84.34 | 77.52 | 240
|  | 16:19 | 85.92 | 79.1 | 240
|  | 16:20 | 87.6 | 80.78 | 240
|  | 16:25 | 95.65 | 88.83 | 240
|  | 16:30 | 101.64 | 94.82 | 240
|  | 16:40 | 111.922 | 105.102 | 240
Summarised results of SDT
Steps | Duration (min) | Discharge (Q) lpm | Drawdow (s) m | Specific Capacity (Q/S) lpm/m | Specific Drawdown (S/Q) m/lpm
Step I | 60 | 157.8 | 12.21 | 12.9238 | 0.077376
Step II | 60 | 207 | 60.04 | 3.4477 | 0.29005
Step III | 40 | 240 | 105.102 | 2.2835 | 0.43793
Observations from the SDT results:
The well is of very high specific capacity and of almost uniform specific drawdown
After STEP I, specific capacity of the well increased
Graphycal Results

## Aquifer Performance Test
AQUIFER PERFORMANCE TEST ON EXPLORATORY WELL |  |  |  |  | CDW 52
Duration |  |  | 1440 | (min) | 24HRS
Constant Discharge Rate |  |  | 120 | (lpm)
Monitoring of pumping water level
Date of test
Static Water Level |  |  | 8.5 | (m) bmp
M.P Top of well casing |  |  | 0.41 | (m) agl
Time in hours | Time (t) since pumping started (min) | Pumping Water Level in m (b.m.p) | Drawdown (S) in (m) | Discharge(Q) in lpm | Remarks
|  | 8.5 |  | 120 | Pumping started at 0900hrs
| 1 | 11.98 | 3.48 | 120
| 2 | 13.56 | 5.06 | 120
| 3 | 14.96 | 6.46 | 120
| 4 | 16.3 | 7.8 | 120
| 5 | 17.42 | 8.92 | 120
| 6 | 19.3 | 10.8 | 120
| 7 | 20 | 11.5 | 120 | Atm temp
| 8 | 21.02 | 12.52 | 120 | Water temp
| 9 | 22.35 | 13.85 | 120
| 10 | 23.13 | 14.63 | 120
| 11 | 24.2 | 15.7 | 120
| 12 | 25.42 | 16.92 | 120
| 13 | 26.09 | 17.59 | 120
| 14 | 26.93 | 18.43 | 120
| 15 | 27.68 | 19.18 | 120
| 16 | 28.32 | 19.82 | 120
| 17 | 28.92 | 20.42 | 120
| 18 | 29.5 | 21 | 120
| 19 | 29.8 | 21.3 | 120
| 20 | 30.16 | 21.66 | 120
| 25 | 31.63 | 23.13 | 120
| 30 | 33.5 | 25 | 120
| 40 | 34.92 | 26.42 | 120
| 50 | 35.56 | 27.06 | 120
| 60 | 35.9 | 27.4 | 120
| 75 | 36.27 | 27.77 | 120
| 90 | 38.91 | 30.41 | 120
| 120 | 40.11 | 31.61 | 120
| 150 | 40.67 | 32.17 | 120
| 180 | 40.96 | 32.46 | 120
| 240 | 41.65 | 33.15 | 120
| 300 | 41.9 | 33.4 | 120
| 360 | 42.27 | 33.77 | 120
| 420 | 42.75 | 34.25 | 120
| 480 | 43.03 | 34.53 | 120
| 600 | 43.46 | 34.96 | 120 | Test concluded at
| 720 | 43.94 | 35.44 | 120
| 840 | 44.3 | 35.8 | 120
| 960 | 44.44 | 35.94 | 120
| 1080 | 44.46 | 35.96 | 120
| 1200 | 44.6 | 36.1 | 120
| 1320 | 44.84 | 36.34 | 120
| 1440 | 45.12 | 36.62 | 120
Aquifer Performance Test (APT) was conducted on CDW52 for a continuos period of 1440 min (24hrs) at constant rate of 120lpm.
At the end of the test, maximum drawdown recorded in the observation well = |  |  |  | 36.62 | m
Time drawdown data thus generated during the course of APT were plotted on semi-logarithmic graph and best fitting straight line was drawn
Fig. 1
1.6667
0.069444
This shows more or less non equilibrium condition
The modified non-equilibrium formula of Theis (1933) was used to compute co-eeficient of Transmissibility (T):
Where:
T = co-efficient of transmissibility in m2/day
Q = Discharge in m3/day
Ds = Change in meters in the drawdown over one log cycle of time [from Fig. 1]
Q = | 120 | lpm = | 0.12 | m3 /m = | 172.8 | m3 /day
Ds = | 11 | ∆S | 11 | m
|  |  |  | T | 2.8767 | m2 /day
K
|  |  |  | S | 2.2989
Hydraulic Conductivity or coefficient of permeability, K = T/b |  |  |  |  | where b is the saturated thickness of the aquifer
Storage coefficient, S can be obtained by selecting any drawdown from the time drawdown curve for a given time and substituting this value in the equation:
Where:
|  |  |  | 4.68e-05 | [for confined aquifers the rage is 0.00005 and 0.005]
[for unconfined aquifers the range is 0.05 to 0.3]
Results:
Therefore the storage co-efficient value obtained clearly indicate that the aquifer is confined.
The computed aquifer parameters indicate that the aquifers are very good to excellent with high yield potential especially when considered in the light of hard rock aquifers
𝑻=(𝟐.𝟑×𝟏𝟕𝟐.𝟖)/(𝟒×𝟑.𝟏𝟒×𝟏𝟏)=𝟐.𝟖𝟖𝒎^𝟐/𝒅𝒂𝒚
𝑺=(𝟐.𝟑×𝟏𝟕𝟐.𝟖)/(𝟒×𝟑.𝟏𝟒×𝟐.𝟖𝟖) 〖𝒍𝒐𝒈〗_𝟏𝟎 (𝟐.𝟐𝟓×𝟐.𝟖𝟖×𝟎.𝟎𝟔𝟗𝟒)/(〖𝟎.𝟏𝟎𝟏𝟒〗^𝟐×𝟐𝟕)=𝟐.𝟑𝟎